## Slide 1: Voltage flickers – sources of flickers, quantifying flickers and mitigation techniques.

## Slide 2
What is a Flicker?

## Slide 3
Voltage flickers –
sources of flickers, quantifying flickers and mitigation techniques.
1 Although voltage flicker is not technically a long-term voltage variation, but the root cause of problems is the same: The system is too weak to support the load.
2 The voltage variations resulting from flicker are often within the normal service voltage range, but the changes are sufficiently rapid to be irritating to certain end users.
3. Low-frequency ac voltage resulted in a “flickering” of the lights. To avoid this problem, a higher 60-Hz frequency was chosen as the standard in North America.

## Slide 4
4.The phenomenon being referred to can be defined as a fluctuation in system voltage that can result in observable changes (flickering) in light output.
5.Because flicker is mostly a problem when the human eye observes it, it is considered to be a problem of perception.

## Slide 6
Flicker signals are usually specified as a percentage of the normal operating voltage. By using a percentage, the flicker signal is independent of peak, peak-to-peak, rms, line-to-neutral, etc.
Typically, percent voltage modulation is expressed by

## Slide 7
The human eye is more sensitive to luminance fluctuations in the 5- to 10-Hz range.
As the frequency of flicker increases or decreases away from this range, the human eye generally becomes more tolerable of fluctuations.

## Slide 8: From Where does flicker Comes?

## Slide 9: Sources of flicker
Typically, flicker occurs on systems that are weak relative to the amount of power required by the load, resulting in a low short-circuit ratio.
This, in combination with considerable variations in current over a short period of time, results in flicker.
As the load increases, the current in the line increases, thus increasing the voltage drop across the line.
This phenomenon results in a sudden reduction in bus voltage.
Depending upon the change in magnitude of voltage and frequency of occurrence, this could result in observable amounts of flicker.

## Slide 10
If a lighting load were connected to the system in relatively close proximity to the fluctuating load, observers could see this as a dimming of the lights.
A common situation, which could result in flicker, would be a large industrial plant located at the end of a weak distribution feeder.
Whether the resulting voltage fluctuations cause observable or objectionable flicker is dependent upon the following parameters:
■ Size (VA) of potential flicker-producing source
■ System impedance (stiffness of utility)
■ Frequency of resulting voltage fluctuations

## Slide 11
ELECTRIC ARC FURNACE
A common load that can often cause flicker is an electric arc furnace (EAF).
EAFs are nonlinear, time-varying loads that often cause large voltage fluctuations and harmonic distortion.
Most of the large current fluctuations occur at the beginning of the melting cycle.
During this period, pieces of scrap steel can actually bridge the gap between the electrodes, resulting in a highly reactive short circuit on the secondary side of the furnace transformer.
This meltdown period can generally result in flicker in the 1.0- to 10.0-Hz range. Once the melting cycle is over and the refining period is reached, stable arcs can usually be held on the electrodes resulting in a steady, three-phase load with high power factor

## Slide 12: Induction Motor
Large induction machines undergoing start-up or widely varying load torque changes are also known to produce voltage fluctuations on systems. As a motor is started up, most of the power drawn by the motor is reactive This results in a large voltage drop across distribution lines.
The most severe case would be when a motor is started across the line. This type of start-up can result in current drawn by the motor up to multiples of the full load current.
An example illustrating the impact motor starting and torque changes can have on system voltage is shown in Fig.
In this case, a large industrial plant is located at the end of a weak distribution feeder. Within the plant are four relatively large induction machines that are frequently restarted and undergo relatively large load torque variations.

## Slide 14
Although starting large induction machines across the line is generally not a recommended practice, it does occur.
To reduce flicker, large motors are brought up to speed using various soft-start techniques such as reduced-voltage starters or variable-speed drives.

## Slide 15: How to Mitigate Flickers

## Slide 16: Mitigation techniques
1. Mitigation alternatives include static capacitors, power electronic-based switching devices, and increasing system capacity.
The particular method chosen is based upon many factors such as the type of load causing the flicker, the capacity of the system supplying the load, and cost of mitigation technique.
2. Flicker is usually the result of a varying load that is large relative to the system short-circuit capacity.
One obvious way to remove flicker from the system would be to increase the system capacity sufficiently to decrease the relative impact of the flicker-producing load.

## Slide 17
3. Upgrading the system could include any of the following: reconductoring, replacing existing transformers with higher kVA ratings, or increasing the operating voltage.
4. Motor modifications are also an available option to reduce the amount of flicker produced during motor starting and load variations.
The motor can be rewound (changing the motor class) such that the speed-torque curves are modified. Unfortunately, in some cases this could result in a lower running efficiency. Flywheel energy systems can also reduce the amount of current drawn by motors by delivering the mechanical energy required to compensate for load torque variations.

## Slide 18
5. Recently, series reactors have been found to reduce the amount of flicker experienced on a system caused by EAFs. Series reactors help stabilize the arc, thus reducing the current variations during the beginning of melting periods.
By adding the series reactor, the sudden increase in current is reduced due the increase in circuit reactance.
6. Series capacitors can also be used to reduce the effect of flicker on an existing system. In general, series capacitors are placed in series with the transmission line supplying the load. The benefit of series capacitors is that the reaction time for the correction to load fluctuations is instantaneous in nature.

## Slide 19
7. Static var compensators (SVCs) are very flexible and have many roles in power systems. SVCs can be used for power factor correction, flicker reduction, and steady-state voltage control, and also have the benefit of being able to filter out undesirable frequencies from the system.
SVCs typically consist of a TCR in parallel with fixed capacitors (Fig. 7.18). The fixed capacitors are usually connected in ungrounded wye with a series inductor to implement a filter.

## Slide 23: Thank You