## Slide 1
Unit 03: Transient Over Voltages and Flickers (6 hrs)
Classification of transients, sources of transient over voltages, computer tools for transient analysis, techniques for over voltage protection.
Voltage flickers – sources of flickers, quantifying flickers and mitigation techniques.

## Slide 2
There are two main sources of transient overvoltages on utility systems: capacitor switching and lightning.
These are also sources of transient overvoltages as well as a myriad of other switching phenomena within end-user facilities. Some power electronic devices generate significant transients when they switch.

## Slide 3: Sources of transient overvoltage

## Slide 5: Capacitor switching operation

## Slide 7
Figure 4.3 shows the phase current observed for the capacitor-switching incident described in the preceding text. The transient current flowing in the feeder peaks at nearly 4 times the load current.

## Slide 12: Cont….
A direct strike to a phase conductor generally causes line flashover near the strike point. Not only does this generate an impulsive transient, but it causes a fault with the accompanying voltage sags and interruptions.
The lightning surge can be conducted a considerable distance along utility lines and cause multiple flashovers at pole and tower structures as it passes. The interception of the impulse from the phase wire is fairly straightforward if properly installed surge arresters are used.

## Slide 15
Figure 4.16 illustrates these principles, which are applied to protect
from a lightning strike.

## Slide 16
The main function of surge arresters and transient voltage surge suppressors (TVSSs) is to limit the voltage that can appear between two points in the circuit.
One of the points to which arresters, or surge suppressors, are connected is frequently the local ground, but this need not be the case.

## Slide 17
Keep in mind that the local ground may not remain at zero potential during transient impulse events.
Surge suppression devices should be located as closely as possible to the critical insulation with a minimum of lead length on all terminals.
While it is common to find arresters located at the main panels and subpanels, arresters applied at the point where the power line enters the load equipment are generally the most effective in protecting that particular load

## Slide 18: Devices for Overvoltage Protection
1. Surge arresters and transient voltage surge suppressors
Arresters and TVSS devices protect equipment from transient overvoltages by limiting the maximum voltage, and the terms are sometimes used interchangeably.
However, TVSSs are generally associated with devices used at the load equipment. A TVSS will sometimes have more surge-limiting elements than an arrester, which most commonly consists solely of MOV (Metal oxide varistors) blocks. An arrester may have more energy-handling capability; however, the distinction between the two is blurred by common language usage.

## Slide 19
MOV arresters have two important ratings. The first is maximum continuous
operating voltage (MCOV), which must be higher than the line
voltage and will often be at least 125 percent of the system nominal voltage.
The second rating is the energy dissipation rating (in joules). MOVs
are available in a wide range of energy ratings. Figure 4.18 shows the typical energy-handling capability versus operating voltages.

## Slide 20: Low-pass filters
Low-pass filters use the pi-circuit principle illustrated in Fig. 4.16 to achieve even better protection for high-frequency transients. For general usage in electric circuits, low-pass filters are composed of series inductors and parallel capacitors.

## Slide 21
This LC combination provides a low impedance path to ground for selected resonant frequencies.
In surge protection usage, voltage clamping devices are added in parallel to then capacitors.
In some designs, there are no capacitors.

## Slide 22: Low-impedance power conditioners
Low-impedance power conditioners (LIPCs) are used primarily to interface with the switch-mode power supplies found in electronic equipment.
LIPCs differ from isolation transformers in that these conditioners have a much lower impedance and have a filter as part of their design

## Slide 23
The filter is on the output side and protects against high-frequency, source-side, common-mode, and normal-mode disturbances (i.e., noise and impulses).

## Slide 24: surge arrester
The three most common surge arrester technologies employed by utilities are depicted in Fig. 4.23. Most arresters manufactured today use a MOV as the main voltage-limiting element. The chief ingredient of a MOV is zinc oxide (ZnO), which is combined with several proprietary ingredients to achieve the necessary characteristics and durability.

## Slide 25: Surge Arresters

## Slide 27
Gaps are necessary with the SiC because an economical SiC element giving the required discharge voltage is unable to withstand continuous system operating voltage.
The development of MOV technology enabled the elimination of the gaps. This technology could withstand continuous system voltage without gaps and still provide a discharge voltage comparable to the SiC arresters

## Slide 28
The gapped MOV technology removes about one-third of the MOV blocks and replaces them with a gap structure having a lightning sparkover approximately one-half of the old SiC technology.
The smaller number of MOV blocks yields a lightning-discharge voltage typically 20 to 30 percent less than a gapless MOV arrester.
Because of the capacitive and resistive interaction of the grading rings and MOV blocks, most of the front-of-wave impulse voltage of lightning transients appears across the gaps.